Technical Specification BA Air Compressor

| Specifications |  |
| --- | --- |
| Type of Compressor | Reciprocating Air Compressors, Electrical operated, Positive displacement with air receiver conforming to IS:7938 (storage tank) |
| Whether compressor ISI Marked | Yes. ISI Marked as per... |
| STANDARD |  |
| Description of Store | Reciprocating Air Compressors - Electrical Operated for General Purpose and Industrial applications and Compressor Consisting of Motor, Piston and Cylinder, with or without Storage Tank etc |
| Air Compressor Confirming to | As per IS 17093: 2019 latest and as per IS 5456: 2006 latest |
| Type of Compressor | Reciprocating Air Compressors, Electrical operated, Positive displacement with air receiver conforming to IS:7938 (storage tank) |
| GENERIC |  |
| Whether compressor ISI Marked | Yes. ISI Marked as per IS:5456 |
| If ISI marked Yes, BIS License number (CM/L .No.) (Must declare, if Non ISI Marked write as "Non ISI Marked | NA |
| Availability of Star Rating | No Star Rating |
| Duty Cycle | Continuous |
| Number of Stages for compression (in numbers) | 2 |
| PRIME MOVER |  |
| Power Rating of Prime Mover (in Kw) - Must declare | 3.7 |
| Power Supply | Three Phase, 415 ± 10% V AC, 50HZ, +5% |
| Type of Prime Mover | TEFC (Totally Enclosed Fan Cooled) Electric Motor |
| Transmission | V Belt |
| PRESSURE |  |
| Rated Discharge Pressure (kg/cm²) | 10.0 to 10.9 |
| Guaranteed Free Air Delivery (FAD) at rated Pressure (CFM), Minimum | 100 |
| COMPRESSOR - AIR PURITY |  |
| Compressed air – Contaminants and purity classes | as per ISO 8573-1:2010 (E) latest |
| Compressed air purity classes for particles | CLASS 1 |
| Compressed air purity classes for humidity and liquid water | CLASS 1 |
| Compressed air purity classes for total oil | CLASS 1 |
| Construction |  |
| Type of Mounting | Tank Mounted |
| Cooling System | Air Cooled |
| Lubrication Type | Oil Lubricated |
| Inter Cooler | With |
| After Cooler | With |
| Moisture Separator | With |
| Oil Separator | With |
| Oil Cooler | Without |
| Dryer Type | Heatless |
| Air Filter | With |
| Noise level in dB | ≤85 |
| Additional Requirement | Not Applicable |
| AIR RECEIVER |  |
| Layout of Air Receiver | Horizontal |
| Capacity of Air Receiver (in Liters), minimum | 220 |
| Maximum Working Pressure (in kg/cm²) | ≤60 |
| COMPRESSOR-COOLER |  |
| Provision of cooler | without Cooler |
| Type of Inter Cooler / After Cooler | Finned and tube type |
| Design of Tube / Plate of Inter Cooler / After Cooler | Finned |
| Material of Shell | Without cooler |
| Material of Tube / Plate | Without cooler |
| Material of Fin | Without cooler |
| COMPRESSOR-OPERATING CONDITIONS |  |
| Minimum Operating Temperature (in deg. C) | -5 |
| Maximum Operating Temperature (in deg. C) | 55 |
| Operating Humidity (in Rh) | 75 |
| Maximum Altitude (in Mtr.) | 1000 |
| COMPRESSOR-ACCESSORIES |  |
| Instrumentation in the scope of supply with each compressor set (Normal requirement) | Yes as per Cl.19.2 of IS:17093 for Air side, Lube oil side and for Cooling water side |
| Instrumentation with each compressor set (Normal requirement) - Air side | Air outlet pressure gauge / transmitter |
| Instrumentation with each compressor set (Normal requirement) - Lube oil side | Temperature gauge/transmitter (optional) |
| Instrumentation with each compressor set (Normal requirement) - Cooling water side | Temperature gauge/transmitter cooling water (optional) |
| Additional instrumentations with each compressor set | Voltmeter |
| Safety devices | Light Switches |
| Indicator | Power-‘On-off’ light indicator |
| Valve and Gauges | Pressure gauges for each interstage manifold and for final air discharge |
| CERTIFICATION |  |
| Warranty on Complete Compressor System (in Years) | 1 |
| Availability of Type Test Report from Central Gov. Lab/NABL Accredited Lab/ILAC Accredited Lab to Prove Conformity of Specification | Yes as per IS 17093:2019 Latest and as per IS 5456:2006 Latest |
| Report No and Date - Must Declare | 2022 |
| Name and address of Lab - Must declare | ASCTL |
| Agreed to furnish all the test reports and certificates | Yes |